## Failure_mode_report.xlsx
| customer_name | building_name | device_type | failure_types | manufacturer | model | note | comment
0 | Caright | 11961999 - Caright | firedeptconnection
1 | Caright | 11961999 - Caright | firedeptconnection | Visual Failure |  |  | Needs an internal and a hydro done. Could not locate the check valve, may be at the rear of the garage. | ['needs', 'check valve']
2 | Caright | 11961999 - Caright | gauge
3 | Caright | 11961999 - Caright | gauge | Visual Failure |  |  | Over 5 years old, it needs to be replaced.
4 | Caright | 11961999 - Caright | gauge
5 | Caright | 11961999 - Caright | gauge | Visual Failure |  |  | Over 5 years old, it needs to be replaced.
6 | Caright | 11961999 - Caright | inspectorstestvalve | Visual Failure |  |  | It needs to be reduced to half inch to correctly test the water flow device. | ['water flow device']
7 | Caright | 11961999 - Caright | panel | Functional Failure | Simplex | 4005 | The 2 batteries which are less than 80%. In prior years it has been stated that the voltage for charging the batteries was low. It still is at 25.9 vdc, tried adjusting pot but the voltage would not get any higher, it should be over 27 vdc. The fire alarm panel needs service, recommend upgrading the Simplex 4005 fire alarm panel since parts are becoming obsolete. | ['fire alarm panel needs service', 'simplex', 'fire alarm panel']
8 | Caright | 11961999 - Caright | panel | Functional Failure | Simplex | 4005 | The 2 batteries which are less than 80%. In prior years it has been stated that the voltage for charging the batteries was low. It still is at 25.9 vdc, tried adjusting pot but the voltage would not get any higher, it should be over 27 vdc. The fire alarm panel needs service, recommend upgrading the fire alarm panel. | ['fire alarm panel needs service', 'fire alarm panel']
9 | Caright | 11961999 - Caright | panel | Functional Failure | Simplex | 4005 | The batteries are only 1.5 years old and load tested at 85%. Battery charger is only at 26.2 vdc and tried adjusting but the charger voltage would not increase. May have to replace cpu or install a new Facp. | ['battery', 'charger voltage', 'may', 'facp']
10 | Caright | 11961999 - Caright | postindicatorvalve | Visual Failure |  |  | The lock is froze up so the Piv could not be exercised, even tried graphite. Recommend cutting off old lock and installing a new lock and put the key in the spare sprinkler box. | ['piv', 'recommend', 'old lock', 'new lock', 'spare sprinkler box']
11 | Caright | 11961999 - Caright | sprinklerhead | Visual Failure |  |  | Sprinkler head is wrapped in tape, the tape needs to be removed. It approximately 30 feet high. | ['sprinkler', 'tape needs']
12 | Caright | 11961999 - Caright | telephonedialer | Functional Failure |  |  | Confirmed with Tyco IS and they stated they received trouble signals but Not alarm signals, need service. | ['confirmed', 'tyco is', 'trouble signals', 'alarm signals']
13 | Grand Total